## Sheet1
Foyle Hospice
All TMVs on site
RP: | Y. Cheung | C. Jeffrey
Calibrated EQ.: | Testo 925
Anton APM200
Thermapen 3
Date |  | Building | Location | Type | Temp. Celcius | Comments | NEW TEMP | COMMENTS
|  | Main | Apartment 3 | WHB | 42
|  | Main | Apartment 3 | Shower | - | Faulty shower
|  | Main | Apartment 2 | WHB | - | TMV Fail
|  | Main | Apartment 2 | Shower | 42
|  | Main | Apartment 1 | WHB | 42
|  | Main | Apartment 1 | Shower | 41
|  | Main | Relatives WC | WHB | 41
|  | Main | Disabled WC (opposite Committee Room) | WHB | - | Isolation valves faulty
|  | Main | Toilet Reception | WHB | - | Isolation valves faulty
|  | Main | Room 1 | WHB | 41 | Isolation valves in bad condition
|  | Main | Room 1 | Shower | 42
|  | Main | Room 1 | WHB | - | Isolation valves faulty
|  | Main | Room 2 | WHB | 41
|  | Main | Room 2 | Shower | - | Faulty shower
|  | Main | Room 2 | WHB | 42
|  | Main | Room 3 | WHB | - | Isolation valves faulty
|  | Main | Room 3 | Shower | 41
|  | Main | Room 3 | WHB | - | Isolation valves faulty
|  | Main | WC Main Corridor | WHB | - | Isolation valves faulty
|  | Main | Nurses Station | WHB | - | TMV Fail, isolation valves in bad condition
|  | Main | Heather Room | WHB | - | No isolation
|  | Main | Heather Room | Shower | 43
|  | Main | Heather Room | WHB | - | No isolation
|  | Main | Treatment Room | WHB | 44
|  | Main | Alpine Room 1 | WHB | - | Isolation valves faulty
|  | Main | Alpine Room 1 | Shower | 43
|  | Main | Alpine Room 1 | WHB | 42
|  | Main | Alpine Room 2 | WHB | 42
|  | Main | Alpine Room 2 | Shower | 41
|  | Main | Alpine Room 2 | WHB | 42
|  | Main | Room 4 | WHB | - | Isolation valves faulty
|  | Main | Room 4 | Shower | 41
|  | Main | Room 4 | WHB | 42
|  | Main | Room 5 | WHB | - | Isolation valves faulty
|  | Main | Room 5 | Shower | 42
|  | Main | Room 5 | WHB | - | Isolation valves faulty
|  | Main | Jacuzzi Room | Bath | 41
|  | Main | Jacuzzi Room | Spray WHB | 38
|  | Main | Jacuzzi Room | WHB | 40
|  | Main | Female Staff Changing | WHB | - | Isolation valves faulty
|  | Main | Female Staff Changing | WHB | 43
|  | Main | Male Staff Changing | Shower | - | Isolation valves faulty
|  | Main | Male Staff Changing | Shower | - | Faulty shower, cartridge required
|  | Main | Male Staff Changing | WHB | - | Isolation valves faulty
|  | Day Centre | Staff WC | WHB | - | TMV Fail
|  | Day Centre | Disabled WC | Shower | 47 | Shower Faulty
|  | Day Centre | Therapy Room | WHB | - | TMV Fail
|  | Day Centre | Doctors Office | WHB | 41
|  | Day Centre | Hairdressing Room | WHB | 43
|  | Day Centre | Nurses Office | WHB | - | TMV Fail
|  | Day Centre | Assisted Bathroom | WHB | - | TMV Fail
|  | Day Centre | Assisted Bathroom | Shower
|  | Day Centre | Female WC | WHB | - | TMV Fail
|  | Day Centre | Female WC | WHB | - | TMV Fail
|  | Day Centre | Male WC | WHB | - | TMV Fail
|  | Day Centre | Male WC | WHB | 43
| r | Day Centre | Copper Room | WHB | 42
|  | Day Centre | Ladies Room | WHB | 36 | -
|  | Day Centre | Public WC | WHB | - | Tap Broken |  | 59
TOTAL COUNT - 59 |  | Recommend TMV to be fitted in Disabled WC WHB
Recommend dead legs to be removed from Assisted Bathroom
Recommend Failed TMVs to be replaced
Recommend Failed Showers to be replaced
Recommend isolation valves to be replaced / fitted where faulty/missing