## Sheet1
Date | Building | Location | Make | Size | Temp. Celci | Comments
All Douglas valves have faulty Isolation built into valves. Reccomend external Isolation
2020-03-05 | Millbrook Court | Toilet/shower | Callefi | 15 | 39
| Millbrook Court | Toilet 1 | ? | 15 | 42 | No isolation
| Millbrook Court | Bedroom 1 | Imix | 15 | 40.7
| Millbrook Court | Kitchen 1 |  |  |  | No TMV for sink, woiudl reccomend as all other kitchens do.
| Millbrook Court | Bedroom 2 | Imix | 15 | 42.1 | Failed failsafe test
| Millbrook Court | Bedroom 3 | Imix | 15 | 39 | Failed failsafe test
| Millbrook Court | Bedroom 4 | Imix | 15 | 42
| Millbrook Court | bedroom 5 | Imix | 15 | 41.5 | Failed failsafe test
| Millbrook Court | Bedroom 6 | Imix | 15 | 40
| Millbrook Court | Bedroom 7 | Imix | 15 | 39.1
| Millbrook Court | Bedroom 8 | Imix | 15 | 40.2
| Millbrook Court | Bathroom 1 | Imix | 15 | 40 | Recommend TMV for bath.
| Millbrook Court | Toilet 2 | ? | 15 | 35.8 | No isolation and cannot adjust temp.
| Millbrook Court | Toilet/shower 2 | ? | 15 | 40.8 | No isolation
| Millbrook Court | Bedroom 9 | Imix | 15 | 40 | Failed failsafe test
| Millbrook Court | Bedroom 10 | Imix | 15 | 40.5 | Failed failsafe test
| Millbrook Court | Bedroom 11 | Ausi mix | 15 | 39
| Millbrook Court | Bedroom 12 | Imix | 15 | 42.2 | Failed failsafe test
| Millbrook Court | Bedroom 15 | Imix | 15 | 39.7 | Failed failsafe test
| Millbrook Court | Bedrrom 14 | Imix | 15 | 39.9 | Failed failsafe test
| Millbrook Court | Bedroom 17 | ? | 15 | 39.2 | Failed failsafe test
| Millbrook Court | Bedroom 16 | Imix | 15 | 39.2 | failed failsafe test
| Millbrook Court | Bedroom 18 | ? | 15 | 39.6 | failed failsafe test
| Millbrook Court | Bedroom 19 | Ausi mix | 15 | 39.5
| Millbrook Court | Toilet 3 | ? | 15 | 42.,5 | No isolation
| Millbrook Court | Bathroom 2 | Douglas | 15 | 42.3 | No isolation. Recommend TMV for bath
| Millbrook Court | Kitchen 2 | Douglas | 15 | 38 | Failed failsafe test and cannot adjust temp.
| Millbrook Court | Toilet 4 | Douglas | 15 | 42.5
| Millbrook Court | Bedroom 21 | Aussi mix | 15 | 40.4
| Millbrook Court | Bedroom 22 | Douglas | 15 | 42.3 | No isolation
| Millbrook Court | Bedrom 23 | douglas | 15 | 39.4 | No isolation
| Millbrook Court | Bedroom 24 | Douglass | 15 | 39.2 | No isolation
| Millbrook Court | Bedroom 25 | Douglass | 15 | 42 | No isolation
| Millbrook Court | Bedroom 26 | Caleffi | 15 | 40.9 | Failed failsafe test
| Millbrook Court | Bedroom 27 | Douglas | 15 | 41 | No isolation
| Millbrook Court | Bedroom 28 | Douglas | 15 | 41.8 | No isolation
| Millbrook Court | Bedroom 29 | Ausimix | 15 | 39.1 | Failed failsafe test
| Millbrook Court | Bedroom 30 | Douglas | 15 | 40 | No isolation
| Millbrook Court | Bathroom 3 | Douglas | 15 | 39 | No isolation, Recommend TMV for Bath
| Millbrook Court | Toilet 5 | Douglas | 15 | 39.7 | No isolation
| Millbrook Court | Kitchen 3 | Bossmix | 15 | 39 | Faulty Isolation/Failed failsafe
| Millbrook Court | Bedroom 31 | Douglas | 15 | 41 | NO isolation
| Millbrook Court | Bedroom 32 | Douglas | 15 | 41 | NO isolation
| Millbrook Court | Toilet 6 | Douglas | 15 | 40 | NO isolation
| Millbrook Court | Bedroom 33 | Sirrus | 15 | 42.5 | Failed failsafe test
| Millbrook Court | Bedrrom 35 | Douglas | 15 | 41.1 | No isolation
| Millbrook Court | Bedroom 34 | Douglas | 15 | 41.1
| Millbrook Court | Bedroom 36 |  |  |  | NO access
| Millbrook Court | Bedroom 37 | Ausi Mix | 15 | 39.4
| Millbrook Court | Bedroom 38 | Ausi mix | 15 | 40.4
| Millbrook Court | Bedroom 39 | Imix | 15 | 39 | Failed failsafe test
| Millbrook Court | Shower room | Imix | 15 | 41.8
| Millbrook Court | Bedroom 40 | Reliance | 15 | 40 | Isolation leaking
| Millbrook Court | bedroom 41 | Reliance | 15 | 41.2 | Failed failsafe
| Millbrook Court | bedroom 42 | Ausi mix | 15 | 40.1
| Millbrook Court | Bedroom 43 | Reliance | 15 | 41
| Millbrook Court | Bedroom 44 | Imix | 15 | 40 | Failed failsafe test
| Millbrook Court | Bedroom 45 | Imix | 15 | 40 | Failed failsafe test
| Millbrook Court | Bedroom 46 | Imix | 15 | 42.5 | Ball fix valves leaking.
| Millbrook Court | Bedroom 47 | Ausi mix | 15 | 41
| Millbrook Court | Bedroom 48 | Imix | 15 | 39.9 | Failed fail safe test
| Millbrook Court | Bedroom 49 |  |  |  | No Access
| Millbrook Court | Bedroom 50 | Ausi mix | 15 | 39.8
| Millbrook Court | Bedroom 51 | Imix | 15 | 40.2 | Failed failsafe test
| Millbrook Court | Bathroom 4 | Douglas | 15 | 36 | No isolation and cannot adjust temp.
| Millbrook Court | Toilet 7 | Douglas | 15 | 32.7 | No isolation and cannot adjust temp.
| Millbrook Court | Kitchen 4 | Ausi mix | 15 | 42.9 | Failed failsafe test
| Millbrook Court | Staff toilet 1 | Ausi mix | 15 | 39.1
| Millbrook Court | Staff shower room | Douglas | 15 | 38.5
| Millbrook Court | Sluice | Imix | 15 | 40.8
| Millbrook Court | Staff toilet 2 | Douglas | 15 |  | Water to TMV isiolated. Several dead legs in room.
| Millbrook Court | Staff toilet 3 | Imix | 15 | 39.6
| Millbrook Court | Staff toilet 4 | Douglas | 15 | 43 | No isiolation
All Douglas valves have faulty Isolation built into valves. Reccomend external Isolation
24.11.20 | Millbrook Court | Toilet/shower | Callefi | 15 | 39 | Failed failsafe test
| Millbrook Court | Toilet 1 | Douglas | 15 | 42 | 2x 15mm isolation needed, new TMV required
| Millbrook Court | Bedroom 1 | Imix | 15 | 40.7 | failed failsafe test, 15mm-1/2 flexi required
| Millbrook Court | Kitchen 1 |  |  |  | No TMV for sink, would reccomend as all other kitchens do.
| Millbrook Court | Bedroom 2 | Imix | 15 | 42.1 | Failed failsafe test, 15mm-1/2 flexi required
| Millbrook Court | Bedroom 3 | Imix | 15 | 39 | Failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Bedroom 4 | Imix | 15 | 42 | failed failsafe test, 15mm-1/2 Fexi required
| Millbrook Court | bedroom 5 | Imix | 15 | 41.5 | Failed failsafe test 15mm-1/2 Flexi required
| Millbrook Court | Bedroom 6 | Imix | 15 | 40 | failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Bedroom 7 | Imix | 15 | 39.1 | failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Bedroom 8 | Imix | 15 | 40.2 | failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Bathroom 1 | Imix | 15 | 40 | failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Toilet 2 | Douglas | 15 | 35.8 | 2x 15mm isolation required, new TMv required
| Millbrook Court | Toilet/shower 2 | Douglas | 15 | 40.8 | 2x 15mm isolation required, new TMv required
| Millbrook Court | Toilet/shower 2 | Mira 915b |  |  | Shower broken
| Millbrook Court | Bedroom 9 | Imix | 15 | 40 | Failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Bedroom 10 | Imix | 15 | 40.5 | Failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Bedroom 11 | Ausi mix | 15 | 39
| Millbrook Court | Bedroom 12 | Imix | 15 | 42.2 | Failed failsafe test, 2x 15mm-1/2 flex required
| Millbrook Court | Bedroom 15 | Imix | 15 | 39.7 | Failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Bedrrom 14 | Imix | 15 | 39.9 | Failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Bedroom 17 | Douglas | 15 | 39.2 | Failed failsafe test, 3x 15mm-1/2 flexi required
| Millbrook Court | Bedroom 16 | Imix | 15 | 39.2 | failed failsafe test, 2x 15mm-1/2 flexis required
| Millbrook Court | Bedroom 18 | Douglas | 15 | 39.6 | failed failsafe test, 2 x 15mm isolation required
| Millbrook Court | Bedroom 19 | Ausi mix | 15 | 39.5 | failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Toilet 3 | Douglas | 15 | 42 | 2x 15mm isolation required, new TMV required
| Millbrook Court | Bathroom 2 | Douglas | 15 | 42.3 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Kitchen 2 | peglar | 15 | 38 | new tmv installed by other contractor
| Millbrook Court | Toilet/shower 3 | Douglas | 15 | 42.5 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedroom 21 | Aussi mix | 15 | 40.4 | failed failsafe
| Millbrook Court | Bedroom 22 | Douglas | 15 | 42.3 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedrom 23 | douglas | 15 | 39.4 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedroom 24 | Douglass | 15 | 39.2 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedroom 25 | Douglass | 15 | 42 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedroom 26 | Caleffi | 15 | 40.9 | Failed failsafe test
| Millbrook Court | Bedroom 27 | Douglas | 15 | 41 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedroom 28 | Douglas | 15 | 41.8 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedroom 29 | Ausimix | 15 | 39.1 | Failed failsafe test
| Millbrook Court | Bedroom 30 | Douglas | 15 | 40 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bathroom 3 | Douglas | 15 | 39 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Toilet 5 | Douglas | 15 | 39.7 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Kitchen 3 | Bossmix | 15 | 39 | 2 x Faulty Isolation/Failed fail safe test, 1x 15mm-1/2 Flexi needed
| Millbrook Court | Bedroom 31 | Douglas | 15 | 41 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedroom 32 | Douglas | 15 | 41 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Toilet 6 | Douglas | 15 | 40 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedroom 33 | Sirrus | 15 | 42.5 | Failed failsafe test
| Millbrook Court | Bedrrom 35 | Douglas | 15 | 41.1 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedroom 34 | Douglas | 15 | 41.1 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedroom 36 | Douglas | 15 | 40 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedroom 37 | Ausi Mix | 15 | 39.4 | Failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Bedroom 38 | Ausi mix | 15 | 40
| Millbrook Court | Bedroom 39 | Imix | 15 | 39 | Failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Shower room | Imix | 15 | 41.8 | failed fail safe test
| Millbrook Court | Shower room | Mira 915b |  | 41
| Millbrook Court | Bedroom 40 | Reliance | 15 | 40 | failed fail safe test, 2x 15mm isolation required
| Millbrook Court | Bedroom 40 | Sirrus shower |  | 42
| Millbrook Court | bedroom 41 | Reliance | 15 | 41.2 | Failed failsafe test
| Millbrook Court | Bedroom 41 | sirrus shower |  | 42
| Millbrook Court | bedroom 42 | Ausi mix | 15 | 40.1 | Failed failsafe test
| Millbrook Court | Bedroom 42 | sirrus shower |  | 42
| Millbrook Court | Bedroom 43 | Reliance | 15 | 41 | Failed failsafe test
| Millbrook Court | Bedroom 43 | sirrus shower |  | 43
| Millbrook Court | Bedroom 44 | Imix | 15 | 40 | Failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Bedroom 44 | Sirrus shower |  | 42
| Millbrook Court | Bedroom 45 | Imix | 15 | 40 | Failed failsafe testa, 15mm-1/2 Flexi required
| Millbrook Court | Bedroom 45 | sirrus shower |  | 42
| Millbrook Court | Bedroom 46 | Imix | 15 | 42.5 | 2x 15mm isolation required
| Millbrook Court | Bedroom 46 | sirrus shower |  | 43
| Millbrook Court | Bedroom 47 | Ausi mix | 15 | 41 | failed fail safe test
| Millbrook Court | Bedroom 47 | Bristan shower |  | 39
| Millbrook Court | Bedroom 48 | Imix | 15 | 39.9 | Failed fail safe test, 15mm-1/2 Flexi required
| Millbrook Court | Bedroom 48 | Sirrus shower |  | 43
| Millbrook Court | Bedroom 49 | imx | 15 | 39 | failed failsafe test, 15mm-1/2 Flexi required
| Millbrook Court | Bedroom 49 | sirrus shower |  | 42
| Millbrook Court | Bedroom 50 | Ausi mix | 15 | 39.8 | failed fail safe test, 15mm-1/2 Flexi required
| Millbrook Court | Bedrooom 50 | sirrus shower |  | 42
| Millbrook Court | Bedroom 51 | Imix | 15 | 40.2 | Failed failsafe test, 15mm-1/2 Flexi needed
| Millbrook Court | Bedroom 51 | sirrus shower |  | 41
| Millbrook Court | Bathroom 4 | Douglas | 15 | 36 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Toilet 7 | Douglas | 15 | 32.7 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Kitchen 4 | Ausi mix | 15 | 42.9 | Failed failsafe test
| Millbrook Court | Staff toilet 1 | Ausi mix | 15 | 40
| Millbrook Court | Staff shower room | Mira 915b |  | 42
| Millbrook Court | Staff shower room | Douglas | 15 | 38.5 | failed failsafe test
| Millbrook Court | Sluice | peglar | 15 | 45
| Millbrook Court | Staff toilet 2 | Douglas | 15 | 41
| Millbrook Court | Staff toilet 3 | Imix | 15 | 39.6 | failed fail safe test, 3x 15mm-1/2 flexis required
| Millbrook Court | Staff toilet 4 | Douglas | 15 | 43 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | Bedroom 20 | Douglas | 15 | 39 | failed failsafe test 2x 15mm isolation required
| Millbrook Court | guest room | douglas | 15 | 40 | 2 x 15mm isolation required, new TMV required
| Millbrook Court | guest room | Mira 915b |  |  | Shower broken
| Millbrook Court DAYCARE | kitchen | imix | 15 | 39 | failed fail safe, 1x iso needed , 3x 15mm to 1/2 flexis
| Millbrook Court DAYCARE | male wc | Douglas | 15 | 39 | failed failsafe test
| Millbrook Court DAYCARE | Female wc | Mira 915b |  |  | water to shower isolated
| Millbrook Court DAYCARE | female wc | douglas | 15 | 39 | 2 x 15mm isolation required, new TMV required
| Millbrook Court DAYCARE | staff wc | Ausi mix | 15 | 42
| Millbrook Court DAYCARE | activity room | Douglas | 15 | 39 | 2 x 15mm isolation required, new TMV required