## Sheet1
Date | Building | Location | Make | Size | Temp. Celci | Comments | Date | Failsafe test | Pass/fail | Comments
2020-03-06 | Sunnyside House | Dining Room 1 | Ausi mix | 15 | 39
|  | Lounge | Sirrus | 15 | 40.8 | Failed failsafe test
|  | D1 WHB | Aussi mix | 15 | 39 | Isolation valve faulty
|  | " Sink | Ausi mix | 15 | 39
|  | D2 WHB | Armatage | 15 | 40 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 40.6 | Failed failsafe test
|  | D3 WHB | Armatage | 15 | 41.7 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 43 | Failed failsafe test
|  | D4 WHB | Armatage | 15 | 40.7 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 39 | Failed failsafe test
|  | D5 WHB | Armatage | 15 | 42.3 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 41 | Failed failsafe test, 2x Faulty ball fix valves
|  | Assisted Bathroom WHB | Armatge | 15 | 39 | Failed failsafe test |  |  | Fail
|  | " Bath | Bossmix | 22 | 39.5 |  |  |  | Fail
|  | D6 WHB | Armtage | 15 | 41.7 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 43 | Failed failsafe test, 2x Faulty ball fix valves
|  | D7 WHB | Ausi mix | 15 | 39 | Failed failsafe test, 2x Faulty ball fix valves
|  | " Sink | Sirrus | 15 | 40.9
|  | D8 WHB | Ausi mix | 15 | 39.8
|  | " Sink | Sirrus | 15 | 43.5
|  | Toilet 1 | Tywford | 15 | 39 | 2 x faulty ball fix valves |  |  |  | 2x faulty iso
|  | Toilet 2 | Tywford | 15 | 40 | Failed failsafe test |  |  | Fail
|  | Visitors Toilet | Armatage | 15 | 39 | Recommend replacing TMV satff complain of fluctuating temp. |  |  |  | Temp now working
|  | D9 WHB | Armatage | 15 | 39 | Failed failsafe test |  |  | Pass
|  | " Sink | Sirrus | 15 |  |  |  |  | Pass
|  | D10 WHB | Ausi mix | 15 | 40.2 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 35 | Cannot adjust Temp faulty TMV
|  | D11 WHB | Armatge | 15 | 40 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 41.6
2020-03-09 |  | D12 WHB | Ausi mix | 15 | 39.6
|  | " Sink | Sirrus | 15 | 40.6 | Failed failsafe test
|  | D13 WHB | Armatage | 15 | 43.5 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 40
|  | D14 WHB | Armatage | 15 | 41.3 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 40.4 | Failed failsafe test
|  | D15 WHB | Ausi mix | 15 | 39
|  | " Sink | Ausi mix | 15 | 40
|  | D16 WHB | Armatage | 15 | 41.5 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 39 | Failed failsafe test
|  | D17 WHB | Armatage | 15 | 40 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 40.7
|  | D18 WHB | Armatage | 15 | 43.7 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 40.9 | Failed failsafe test
|  | D19 WHB | Imix | 15 | 41 | Failed failsafe test |  |  | Pass
|  | " Sink | Ausi mix | 15 | 39 |  |  |  | Pass
|  | D20 WHB | Armatage | 15 | 44 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 41 | Failed failsafe test
|  | D21 WHB | Reliance | 15 | 39 |  |  |  | Pass
|  | " Sink | Sirrus | 15 | 40 | Failed failsafe |  |  | Pass
|  | D22 WHB | Armatage | 15 | 41 | Failed failsafe
|  | " Sink | Ausi mix | 15 | 39
|  | Assisted Bathroom 2 WHB | Armatage | 15 | 41 | Failed failsafe test |  |  | Fail
|  | " Bath | Bossmix | 22 | 40 |  |  |  |  | Faulty iso on cold
|  | D23 WHB | Armatage | 15 | 39 | Failed failsafe
|  | " Sink | Sirrus | 15 | 39 | Failed failsafe
|  | D24 WHB | Armatage | 15 | 42 | Failed failsafe
|  | " Sink | Sirrus | 15 | 33 | Failed failsafe, could not adjust temp.
|  | Assisted Bathrrom 3 WHB | Ausi mix | 15 | 40 |  |  |  | Pass
|  | " Bath | Bossmix | 22 | 39 |  |  |  | Pass
2020-03-10 |  | D27 WHB | Armatage | 15 | 42 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 40 | Failed failsafe test
|  | D28 WHB | Armatge | 15 | 41 | Failed failsafe test |  |  | Pass
|  | " Sink | Sirrus | 15 | 42 | Failed failsafe test, 2x faulty ball fix valves |  |  |  | 2x faulty iso
|  | D29 WHB | Sirrus | 15 | 41 | Failed failsafe test
|  | " Sink | Saracen | 15 | 38 | Failed failsafe test, 2x faulty ball fix valves
|  | D30 WHB | Bristan | 15 | 42 | Failed failsafe, 2x faulty ball fix valves
|  | " Sink | Ausi mix | 15 | 40 | 2x faulty ballfix valves
|  | D31 WHB | Armatge | 15 | 41 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 40.5 | Failed failsafe test, 2x faulty ball fix valves
|  | D26 WHB | Armatage | 15 | 42 | Failed failsafe test
|  | " Sink | Ausi mix | 15 | 40
|  | Staff toilet 1 | Armatage | 15 | 40.8 | Failed failsafe |  |  | Pass
|  | Cleaners store 1 | Reliance | 15 | 42 |  |  |  | Pass
|  | D34 WHB | Armatage | 15 | 41.8 | Failed failsafe
|  | " Sink | Sirrus | 15 | 39 | 2x faulty ball fixe valves
|  | D32 WHB | Armatge | 15 | 42 | Failed failsafe
|  | " Sink | Sirrus | 15 | 40.5 | Failed failsafe, 2x faulty ball fix valves
|  | D33 WHB | Armatage | 15 | 41.2 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 40.8
|  | D25 WHB | Armatage | 15 | 41 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 39 | Failed failsafe test, 2 x faulty ball fix valves
|  | D39 WHB | Armatage | 15 | 41.5 | Failed failsafe test |  |  | Fail
|  | " Sink | Sirrus | 15 | 42.2 | Failed failsafe test |  |  | Fail
|  | D38 WHB | Armatage | 15 | 41 | Failed failsafe test |  |  | Fail
|  | " Sink | Sirrus | 15 | 41.8 | 2x faulty ball fix valves |  |  |  | 2x faulty Iso
|  | D37 WHB | Armatage | 15 | 40.8 | Failed failsafe test |  |  | Fail
|  | " Sink | Sirrus | 15 | 40.6 | 2x faulty ball fix, TMV leaking |  |  | Fail | 2x faulty Iso
|  | D36 WHB | Armatage | 15 | 40 | Failed failsafe test |  |  | Fail
|  | " Sink | Sirrus | 15 | 39.9 | Failed failsafe |  |  | Pass
|  | D45 WHB | Armatage | 15 | 42 | Failed failsafe test |  |  | Failed | Faulty iso on hot
|  | " Sink | Sirrus | 15 | 39.1 |  |  |  | Pass
|  | D44 WHB | Armatage | 15 | 39 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 42 | Failed failsafe test
2020-03-12 |  | D43 WHB | Armatage | 15 | 43 | Failed failsafe test
|  | " Sink | Assi mix | 15 | 38.5 | 1x faulty ball fix valve
|  | D42 WHB | Armatage | 15 | 39 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 39 | Failed failsafe test
|  | D41 WHB | Armatage | 15 | 39.4 | Failed failsafe test
|  | " Sink | Sirrus | 15 | 39 | Failed failsafe test, 2x faulty ball fix valves
|  | D40 WHB | Armatage | 15 | 39 | Failed failsafe test |  |  | Fail
|  | " Sink | Sirrus | 15 | 40 | Failed failsafe test |  |  |  | TMV replaced by MTC
|  | D35 WHB | Armatage | 15 | 41 | Failed failsafe test |  |  | Fail
|  | " Sink | Sirrus | 15 | 33 | 2x faulty ball fix valves, could not adjust temp. |  |  |  | 2x faulty Iso
|  | Staff toilet 2 | Ausi mix | 15 | 41
|  | Cleaners Store 2 | Imix | 15 | 43
|  | Family Room WHB | Imix | 15 | 39.7 | Failed failsafe test |  |  | Fail
|  | " Sink | Aussi mix | 15 | 39.7
|  | Dining Room 2 | Sirrus | 15 | 41.8 | Failef failsafe test, x2 faulty ball fix valves
|  | Hair Dressers | Ausimix | 15 | 40 | 1x faulty ball fix valve |  |  |  | faulty iso
|  | " | Ausi mix | 15 | 39 | 1x faulty ball fix valve |  |  |  | faulty iso
|  | Laundry | Imix | 15 | 39 |  |  |  | Pass
|  | Male Wc | Aussi mix | 15 | 39 |  |  |  | Pass
|  | Kitchen | Ausi mix | 15 | 38.5 | Failed failsafe |  |  | Fail
|  | " | Ausi mix | 15 | 38.5 |  |  |  | Pass
|  | Female WC | Sirrus | 15 | 39 |  |  |  | Pass